## Tutorial
Estimate Quantity (only Figures) | Item Detailed Specification Description | Work Type eg. Earth Work, Electrical works.. etc ( upto 200 Characters) | Item Short Description ( upto 100 Characters) | APSS / Morth Cl. Number ( upto 200 Characters) | Rate (INR) ( Upto 2 Decimals ) | UOM ( upto 50 Characters) | Amount (INR) ( Upto 2 Decimals )
4500 | CONDUIT PIPE Supply and fixing of 25mm outer dia 2.20 mm thick Heavy grade PVC pipe (ISI MARK) concealed in Roof Slabs with all required MS deep boxes and all accessories including and labour charges etc., complete. Makes:- Sudhakar/ Modi. Supply and fixing of 25mm outer dia 2.20 mm thick Heavy grade PVC pipe (ISI MARK) concealed in Roof Slabs with all required MS deep boxes and all accessories including and labour charges etc., complete. Makes:- Sudhakar/ Modi. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 70.52 | RM | 317340
600 | Supply and Fixing of 32mm outer dia Medium grade ( 2.1 mm Thick ) P.V.C. pipe (ISI MARK) concealed in wall with all required MS Deep Boxes and all accessories including masonary work for light, fan and separate plug point with MS modular switch box including all labour charges etc., complete. for EPABX, LAN, and CCTV, Run of mains, light, fan points. Makes:- Sudhakar | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 94.3 | RM | 56580
600 | Supply and Fixing of 20 mm outer dia 2.10 mm thick Heavy grade PVC pipe (ISI MARK) concealed in Roof Slabs with all required MS deep boxes and all accessories including and labour charges etc., complete. Makes:- Sudhakar | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 60.28 | RM | 36168
2000 | Supply and fixing of 25mm outer dia Medium grade (1.8 mm thick) P.V.C. pipe (ISI MARK) concealed in wall with all required MS junction boxes and all accessories including masonary work for light, Fan and separate plug point with MS Modular switch box including all labour charges etc., complete for EPABX, LAN, and CCTV, Bell, light, Fan points. Makes:- Sudhakar/ Modi. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 78.3 | RM | 156600
300 | Supply and erecting MS galvanished Fan hook box with hook in RCC slab including all Labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 60 | Nos | 18000
800 | WIRING Wiring with 2 runs of 22/0.3mm ( 1.5 Sq.mm) FRLS P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate including all labour charges etc., complete. (for Residential Building) Makes of wires:- Finolex / RR kabel /KEI / Anchor / Polycab / Havells /Power Flex / RPG / Orbit / V-Guard. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 491.8571 | PTS | 393485.7143
12 | Wiring with 2 runs of 22/0.3mm ( 1.5 Sq.mm) FRLS P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate including all labour charges etc., complete ( Residential Building) for Staircase points. ( 2 way Switch ). Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / /Power Flex / RPG / Orbit / V-Guard. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 670.5333 | PTS | 8046.4
600 | Wiring with 3 runs of 1.5 sq.mm FRLS P.V.C. insulated flexible copper cable (phase, neutral, earth) in the existing conduit pipe with 6 Amps Modular type switch, and 6 A 3/2 pin Modular type socket with cover plate on common switch board etc., complete. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells /Power Flex / RPG / / Orbit / V-Guard. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 290 | PTS | 174000
150 | Wiring with 2 of 22/0.3mm ( 1.5 Sq.mm) FRLS P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control and MS boxes with cover plate fixing on separate board including all labour charges etc., complete. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / GM Four Five / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 461.5333 | PTS | 69230
300 | Wiring with 2 of 22/0.3mm (1.5 Sq.mm) FRLS P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Modular switch control- 3nos and 6A, 3/2 pin Modular sockets - 3 nos fixing on separate board including all labour charges etc., complete. ( for LABs & Computer Use ) Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells //Power Flex / RPG / Orbit / V-Guard. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 892 | PTS | 267600
200 | S&D of 16A/6A, 2 in one socket with 16A switch control modular type with MS flush boxes with front cover plate including all labour charges etc., complete. Makes of switches:- Legrand Myrius / Anchor Roma viola / Cabtree Thames Platinum / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 980 | NOS | 196000
15000 | RUN of MAINS Supply and run of 1 of 22 /0.3mm (1.5 Sq.mm) FRLS P.V.C. insulated flexible copper cable in existing pipe for earth continuity including all labour charges etc., complete. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / GM / Million / HPL / Goldmedal / Kundancab /Power Flex / RPG / Sun Cab / Fortune Art / Great white / Orbit / V Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 20.996 | RM | 314940
2000 | Supply and run of 3 of 1.5 sq.mm (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing MS conduit pipe for sub-circuits including labour charges etc., complete as required for small switch boards. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / GM / Million / HPL / Goldmedal / Kundancab /Power Flex / RPG / Sun Cab / Fortune Art / Great white / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 62.94 | RM | 125880
6000 | Supply and run of 1 of 36/0.3mm (2.5 Sq.mm) F.R.L.S P.V.C. insulated flexible copper cable in existing pipe for mains inlcuding all labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 29.414 | RM | 176484
1200 | Supply and run of 2 of 2.5 sq.mm (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing MS conduit pipe for individual ligting circuits including labour charges etc., complete as required for switch boards. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 58.732 | RM | 70478.4
9000 | Supply and run of 3 of 2.5 sq.mm (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing MS conduit pipe for individual ligting circuits including labour charges etc., complete as required for switch boards. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 88.242 | RM | 794178
6000 | Supply and 2 runs of 4.0 sq mm (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing conduit pipe for run of mains including labour charges etc., complete as required including labour charges for 16A sockets. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 82.128 | RM | 492768
5000 | Supply and 3 runs of 4.0 sq mm (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing conduit pipe for run of mains including labour charges etc., complete as required including labour charges for 16A sockets. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 123.192 | RM | 615960
600 | Supply & run of 3 of 6.0 Sqmm (84/0.3mm) (phase neutral and earth) FRLS PVC insulated flexible copper cable in existing MS conduit pipe for run of mains including labour charges etc. complete for AC points & SDB's etc as required. Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 179.892 | RM | 107935.2
2500 | Supply and run of 5 of 6 Sq mm (phases, neutral and earth) FRLS PVC insulated flexible copper cable in existing MS conduit pipe for circuits including labour charges etc. complete as required for run of mains from Lighting panel board to TPN DB'S with pin type lugs and connections. [for LDBs] Makes of wires:- KEI / Anchor / Polycab / Havells //Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 299.82 | RM | 749550
300 | Supply & run of 2 of 10.0 Sqmm (phases, neutral and earth) FRLS PVC insulated flexible copper cable in the existing conduict pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 181.8 | RM | 54540
2000 | Supply & run of 5 of 10.0 Sqmm (phases, neutral and earth) FRLS PVC insulated flexible copper cable in the existing conduict pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires:- Finolex / RR kabel / KEI / Anchor / Polycab / Havells / Power Flex / RPG / Orbit / V-Guard. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 454.5 | RM | 909000
100 | Supply and fixing of 1 or 2 modular GI box concealed in wall with modular cover frame with all required accessories including masonary work and all labour charges etc., complete of Makes: Legrand Myrius / Cabtree Thames Platinum / GM Four Five / Million Logus / Gold Medal Curve / CPL / Panasonic Vision / Salzer S 90 Series. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 165.96 | Each | 16596
80 | Supply and fixing of 4 modular GI box concealed in wall with modular cover frame with all required accessories including masonary work and all labour charges etc., complete of Makes: Legrand Myrius / Cabtree Thames Platinum / GM Four Five / Million Logus / Gold Medal Curve / CPL / Panasonic Vision / Salzer S 90 Series. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 239.56 | Each | 19164.8
40 | Supply and fixing of 8 modular GI box concealed in wall with modular cover frame with all required accessories including masonary work and all labour charges etc., complete of Makes: Legrand Myrius / Cabtree Thames Platinum / GM Four Five / Million Logus / Gold Medal Curve / CPL / Panasonic Vision / Salzer S 90 Series. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 398.83 | Each | 15953.2
20 | Supply and fixing of 12 modular GI box concealed in wall with modular cover frame with all required accessories including masonary work and all labour charges etc., complete of Makes: Legrand Myrius / Cabtree Thames Platinum / GM Four Five / Million Logus / Gold Medal Curve / CPL / Panasonic Vision / Salzer S 90 Series. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 491.63 | Each | 9832.6
40 | DISTRIBUTION BOARDS Supply and fixing single phase DB in sheet steel enclosure with metallic plug and socket with 1 No. 20/32A,10KA 'c' curve SPMCB (Motor characteristics MCBs) control including making connections etc., complete concealing in wall for A.C. points etc. Makes : Legrand / Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 1610 | NOS | 64400
3 | SPN 6 way D.B with IP-43, 63A FP MCB - 1 No for incomer, 10kA-6-32A SP MCBs - 6 Nos for outgoing. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 4245 | NOS | 12735
40 | Supply and fixing of TPN 4 way distribution board IP-43 (8+12 Module) with provision to accommodate the ELCB incomer and suitable for single pole outgoing MCB's in sheet Steel enclosure with 32A 4 pole MCB as incomer and 12 No of 6 to 32 Amps single pole, 10 KA breaking capacity 'c' Curve MCB outgoings including making connections etc., complete concealing in wall. (LIGHTING DB's) Makes : Legrand / Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 7023.5 | NOS | 280940
40 | Supply and fixing of TPN 4 way distribution board IP-43 (8+12 Mofule) with provision to accommodate ELCB as incomer and suitable for single pole outgoing MCB's in sheet Steel enclosure with 63 Amps 4 pole MCB as incomer and 12 No of 6 to 32 Amps single pole, 10 KA breaking capacity 'c' curve MCBs as outgoings including making connections etc., complete concealing in wall. (POWER DB's) Makes : Legrand / Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 8108.5 | NOS | 324340
12 | Supply and fixing TPN - 8 way Vertical type Distribution board with IP-43 Protection (Metal Door) suitable to accommodate MCCB as incomer and single/three pole MCBs as outgoings with 125A, 4Pole 25 kA MCCB as incomer with 6No of 40/63A, 10 KA TP MCBs 'c' curve and 6 No, 6-32A, 10 kA SP MCBs 'c' curve as outgoing including making connections and labour charges etc., complete concealing in wall. Makes : Legrand / Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 33418.5 | NOS | 401022
6 | Supply and Installation of 125 Amps TPN MCCB with cable end boxes on suitable angle iron frame work for the areas mentioned in the drawings including all Labours charges, massonry work etc. complete for finished item of work. Makes: L&T/Siemens/ Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 11200 | NOS | 67200
80 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 600 | NOS | 48000
10 | EARTHINGS Providing independent earthling by excavating a trench to a depth of 2.5 M in all soils, as per size specified in the Data, using 100mm dia Heavy Gauge C.I ( Cast iron ) pipe of 2.5 Mtrs length with Heavy gauge Flange with necessary accessories including filling with Bentonite powder and all labour charges etc., complete. ( for Main Panels and DG sets ) | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 4740.4 | NOS | 47404
500 | Supply and run of No. 8SWG GI wire including cost of all accessories and labour charges etc complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 16.132 | RM | 8066
200 | Supply and Run of 25mm x 6mm Copper Strip including cost of all accessories and labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 830.31 | RM | 166062
500 | FIXTURES Supply, Transportaton, and fixing of 16W, 1200mm length, 1665 lumins, LED tube light, input voltage AC 240 Volts with ≥0.95 PF with driver and frosted cover etc complete with 5 years warranty. Makes: Syska / Philips / / Anchor / GE / Crompton / Bajaj / VIN LED / Halonix / Surya / BLU / Kripa / Fortune / MIC / Semtronics., | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 1214.4 | NOS | 607200
100 | Supply and fixing of BH/SBH in lieu of ceiling rose with 1 NO 3-5 W bulb with connections etc., complete with labour charges (Gold Medal/ Anchor / Million ) | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 11 | NOS | 1100
25 | Supply and fixing of calling bell on 6"x 8" decolam block including giving connections, cost of all accessories and all labour charges etc., complete. Make: Gold Medal/ Anchor / Million | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 174.52 | NOS | 4363
300 | Supply, Transportation of Ceiling fan 48"(1200mm) ceiling fans with 3 blades & double ball bearings with out Regulators and all standard accessories and giving connections etc., complete. Make: Crompton / Orient. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 1780 | NOS | 534000
300 | Supply and fixing of modular Electronic step type fan regulator hum free step type socket size with MS box, front plate in the existing switch board ( Modular Type ) Make: Anchor roma / MK / Cabtree / Salzar / Legrand / Mosaic model as per Dept., Direction. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 378 | NOS | 113400
300 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 116 | NOS | 34800
300 | Labour charges for Fixing of Ceiling fan including giving connections with twin core wire etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 130.4 | NOS | 39120
50 | Supply,Transportation of Light duty exhaust fan 12"(300 mm) size1350 rpm with metal blades wiremesh with all accessories etc complete Makes: Crompton / Bajaj Bahar WG / Havells Ventil Air-DB / Orient hill air / MIIT. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 1450 | NOS | 72500
50 | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 541.65 | NOS | 27082.5
50 | Supply and fixing of louver shutter suitable for 12" Exhaust fan including all labour charges etc complete with connections and colouring matching to the wall with enamel paint. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 257.5 | NOS | 12875
300 | U.G CABLES Supply of the Following PVC XLPE armoured cable 1100 V Grade with ISI mark stranded / solid, aluminimum conductor complete Make: RPG/ POLY CAB/ Havells/Finolex/ Paragan / Unicab/ V-Guard/ fortune Art EBXL. 3.5 Core 50 Sq.mm. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 280 | RM | 84000
300 | U.G CABLES Supply of the Following PVC XLPE armoured cable 1100 V Grade with ISI mark stranded / solid, aluminimum conductor complete Make: RPG/ POLY CAB/ Havells/Finolex/ Paragan / Unicab/ V-Guard/ fortune Art EBXL. 4.0 Core 16 Sq.mm. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 140 | RM | 42000
300 | Supply, Transportation and laying XLPE armoured under ground HT cable of size 3 Core 185.00 Sqmm 11KV grade of make Torrent / Universal / Polycab / Havells / KEI / RPG / Unicab. with ISI mark standard / Solid alluminium conductor etc., complete by making trench in all soils up to 0.90Mtr deep and filling the Sand at the bottom of trench before laying the cable and emmbedding the cable complete on sand layer and bricks placed on top of the cable width wise all over the run and back filling the exacavated earth without stones and making the surface proper with 15cm crown on the top duly providng root indicators at every 8 Mtrs embeded in CC as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 1859.53 | RM | 557859
300 | Earth work excavation of Trench in hard ground soil, laying of U.G cables of size up to 70 Sqmm on sand cusion covering the cable with bricks and back filling of Trench duly providing route indicator (as per general instruction S.No. 14 of SSR) embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 144.6748 | RM | 43402.44
300 | Labour charges for run of U.G cable on wall / existing pipe with necessary fixing arrangments such as saddles, clamps,wooden separators etc., (as directed by departmental official) for the cables. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 35.7 | RM | 10710
50 | CABLE GLANDS: S&fixing of heavy duty flange type brass cable glands of following sizes for PVC armoured cables with brass washers, earth tag etc complete including all labolur charges. 25 to 50Sq.mm | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 138 | NO | 6900
50 | CABLE GLANDS: S&fixing of heavy duty flange type brass cable glands of following sizes for PVC armoured cables with brass washers, earth tag etc complete including all labolur charges. up to 16 Sq.mm | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 94 | NO | 4700
30 | ALUMINIUM LUGS: Supply and fixing of crimping type Aluminium lugs confirming to IS specifications for following cables including nuts and bolts with connections. 50Sq.mm | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 20 | NO | 600
30 | ALUMINIUM LUGS: Supply and fixing of crimping type Aluminium lugs confirming to IS specifications for following cables including nuts and bolts with connections. 35Sq.mm | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 17 | NO | 510
30 | ALUMINIUM LUGS: Supply and fixing of crimping type Aluminium lugs confirming to IS specifications for following cables including nuts and bolts with connections. 16 Sq.mm | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 12 | NO | 360
10 | STREET LIGHTS Supply and transportation of 150 W LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having efficacy >120 lumines/watt, System efficacy >95lm/W and junction temprature < 70°C, with Ingrees protection IP65, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection ≥ 5KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete a) LUMINAIRE MAKE :PHILIPS (GREEN LINE) / OSRAM / SCHREDER (BRIKA) / GE / VIN (STO) / CROMPTON (LEXUS+) / BAJAJ (EDGE+) / HALONIX (LUMOS - SUPER) / HAVELLS (ENDURA CITYLINER NEO) b) LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 16518 | NOS | 165180
10 | Fixing of LED street light luminary with 1.0 Mtr., 25mm Nominal Bore Medium grade G.I.Pipe bracket and anti tilting MS flat etc., including giving connections and labour charges etc., complete. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 460.925 | NOS | 4609.25
600 | TV WIRING Supply and laying of RG6 co-axial cable in the existing metallic/non metallic conduit pipe with connections etc.,complete for TVs and CCTV Net work. Makes: Finolex/ Million / Gold Medal / Anchor / Polycab | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 24 | RM | 14400
120 | Supply and fixing of TV outlet Modular type in existing MS/modular box with modular front cover plate with screws connections etc., complete. Makes: GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 233 | NOS | 27960
6 | WATER COOLERS Supply and fixing of water cooler fully stainless steel of capacity 60/120 to be operated on single phase supply with ISI mark. Makes Blue star / Voltas / Usha. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 42994 | NOS | 257964
200 | EPABX - TELEPHONE WIRING Supply and laying of 2 pair telephone wire 0.5mm copper in the existing metallic/non metallic conduit pipe with connections etc., complete. Makes: Finolex / Delton / Surabi / Polycab | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 17.564 | RM | 3512.8
6 | Supply and fixing of 2 Line telephone jack socket model modular type with connector front and back plate in existing modular box with screws connections etc., complete. Makes: Legrand Myrius / Cabtree Thames Platinum / Million Logus /Gold Medal Curve / GM Four Five / Anchor Roma viola / CPL / Panasonic Vision. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 229.32 | NOS | 1375.92
300 | LAN Supply and termination of cat-6 RJ 45 out lets including dual face plate of Makes: D Link / AMP / | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 404.32 | NOS | 121296
10000 | Supply and laying of Cat 6 UTP cable including all taxes etc complete. Makes: D Link / AMP / Molex / | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 34.59 | RM | 345900
48 | Supply and fixing of 12 U Floor mounting net work Rack with power spike including all accessories etc., complete. (HCL Vall / D-Link /AMP / Krone) | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 6772 | RM | 325056
2 | MAIN POWER PANEL Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted MV panel made out of No.14/16 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN with suitable bus bars (with rating of 0.8A/ Sqmm) supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves. The metering shall be provided as specified. The panel shall have short-circuit with standing capacities of minimum 50KA and consists of switchgear as mentioned below.The panel shall be got manufactured from the manufacturers of CPRI test certificate only. The panel shall be mounting on U channels including supply and fixing including painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 282997 | NOS | 565994
2 | MAIN LIGHTING PANEL Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted MV panel made out of No.14/16 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN with suitable bus bars (with rating of 0.8A/ Sqmm) supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves. The metering shall be provided as specified. The panel shall have short-circuit with standing capacities of minimum 50KA and consists of switchgear as mentioned below.The panel shall be got manufactured from the manufacturers of CPRI test certificate only. The panel shall be mounting on U channels including supply and fixing including painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 189000 | NOS | 378000
3 | SUB FLOOR POWER PANEL Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted MV panel made out of No.14/16 gauge CRCA sheet steel after 7 tank process and painting Incomer : 400A Four Pole MCCB, 50 KA - Make: L&T d sine Model/Siemens/Schneider - 1 No with powder coating. The panel shall consists of suitable rating TPN with suitable bus bars (with rating of 0.8A/ Sqmm) supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves. The metering shall be provided as specified. The panel shall have short-circuit with standing capacities of minimum 50KA and consists of switchgear as mentioned below.The panel shall be got manufactured from the manufacturers of CPRI test certificate only. The panel shall be mounting on U channels including supply and fixing including painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 190000 | NOS | 570000
3 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted MV panel made out of No.14/16 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN with suitable bus bars (with rating of 0.8A/ Sqmm) supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves. The metering shall be provided as specified. The panel shall have short-circuit with standing capacities of minimum 50KA and consists of switchgear as mentioned below.The panel shall be got manufactured from the manufacturers of CPRI test certificate only. The panel shall be mounting on U channels including supply and fixing including painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 260000 | NOS | 780000
6 | V - FIRE EXTINGUISHERS Supply and fixing of ISI mark (IS:15683) Mono ammonium phosphate powder 90 (MAP) 6 Kg Fire extinguisher, stored pressure type, pressure gauge, gross wt. 9.4 kg, empty wt.3.4 kg, Discharge time minimum 13 sec, controllable discharge mechanism, range min. 4 mts applicable on classes A,B, C & electrically started fire, A rating - 4 A, B rating -34 B, can construction: Deep drawn and Co2 mig welding, Valve construction: Forging & Machining, internal coating of can: Epoxy powder coating, External coating of Can:Epoxy polyster powder coating, sheet metal thickness:1.60mm, Helium leak detection tested with 5 years warranty Including transportation, all taxes and all labour charges etc complete. Makes: Safex / Kenex / Bharat / Reliance. ( SSR - 15-16 - 9.4.8 ) | Electrical works | Electrification Works for 1 Tutorial Block | as per tender document | 6300 | NOS | 37800
13383009.2243